[image: image1.png]




      

  Queen                                                         

  Anne’s                                                  

  County
                                                     
County Commissioners:

Steven J. Arentz, At Large
David L. Dunmyer, District 1

Bob Simmons, District 2

Philip L. Dumenil, District 3

Dave Olds, District 4

Department of PLANNING & ZONING  

110 Vincit Street, Suite 104
Centreville, MD 21617

Telephone Planning: (410) 758-1255

Fax Planning: (410) 758-2905

Telephone Permits: (410) 758-4088

Fax Permits: (410) 758-3972

NOTICE TO:

HOMEOWNERS AND BUILDERS.

EFFECTIVE NOVEMBER 1, 2011……
Queen Anne’s County has adopted the 2009 International Energy Conservation Code as the energy code standard. Chapter 4, on residential energy efficiency, was adopted in its entirety. The provisions of this code require that the builder demonstrates the air sealing and insulation of the building thermal envelope. 

Please indicate which of the two options you choose to comply with:


Blower door test per 402 .4.2.1 specifications 

(prior to final inspection). 

OR


Insulation Installation Certification per table 402.4.2.

(Certificate from Installer required certifying compliance with Table)
Additionally;
DUCT BLAST TESTING IS MANDATORY UNDER THE 2009 IECC. 

A certificate of compliance is required prior to final inspection.

IECC Section 403.2.2 Sealing (Mandatory). All ducts, air handlers, filter boxes and building cavities used as ducts shall be sealed. Duct tightness shall be verified by either of the following:

	1. Post construction test: Leakage to outdoors shall be

less than or equal to 8 cfm (226.5 L/min) per 100 ft2

(9.29 m2) of conditioned floor area or a total leakage

less than or equal to 12 cfm (12 L/min) per 100 ft2

(9.29 m2) of conditioned floor area when tested at a

pressure differential of 0.1 inches w.g. (25 Pa) across

the entire system, including the manufacturer’s air

handler enclosure. All register boots shall be taped or

otherwise sealed during the test.


	2. Rough-in test: Total leakage shall be less than or

equal to 6 cfm (169.9 L/min) per 100 ft2 (9.29 m2) of

conditioned floor area when tested at a pressure differential  of 0.1 inches w.g. (25 Pa) across the roughed in system, including the manufacturer’s air handler enclosure. All register boots shall be taped or otherwise sealed during the test. If the air handler is not

installed at the time of the test, total leakage shall be

less than or equal to 4 cfm (113.3 L/min) per 
100 ft2(9.29 m2) of conditioned floor area.



